## B1 Lot 1 - Camp 4
BGD-UNHCR RFP 3830 Technical Bill of Quantities (no prices) – Lot 1 – RHEC Camp 4 Design, BoQ, Supply, Installation, Testing and Commissioning of Solar PV Hybrid Power Systems – Two RHECs, Cox’s Bazar
Annex B1 – Technical BoQ
SL | Item | Specification offered (make, model, key ratings) | Unit | Qty | Country of origin | Stock availability / lead time
1 | Solar PV modules – Monocrystalline N-Type or better/advanced technology, minimum 550 Wp per module, with total installed capacity meeting the design requirements (minimum 25 kWp). The stated specification shall be considered the minimum acceptable standard. |  | Pcs
2 | Mounting structure incl. roof fixing and any structural strengthening |  | Lot
3 | DC combiner / PV junction boxes with isolators, gPV fuses and SPDs |  | Set
4 | PV (DC) cables and MC4 connectors |  | Meter
5 | Three-phase hybrid inverter configuration with minimum combined inverter capacity of 20 kW. Bidders may propose one or multiple inverter units to achieve the required capacity and redundancy requirements. |  | Set
6 | LiFePO₄ battery energy storage system incl. BMS, racks/cabinet (≥ 150 kWh gross / ≥ 105 kWh usable) |  | Set
7 | Battery area works: enclosure/ventilation, smoke & heat detection with alarm |  | Lot
8 | Fire extinguishers, Class C (CO₂ / clean agent) |  | Pcs
9 | AC distribution board, automatic changeover/ATS, breakers and integration with existing MDB |  | Set
10 | AC cables incl. trenching / conduit |  | Meter
11 | Earthing system (array, inverter, BESS, boards) - Complete earthing system for solar array, inverter, battery energy storage system (BESS), distribution boards and all associated metallic structures. Design, installation and testing shall comply with the latest edition of BNBC and applicable IEC standards. Earthing bore depth shall be not less than 40 ft (12 m), subject to achieving the required earth resistance value. |  | Lot
12 | Lightning protection system - Complete lightning protection system designed and installed in accordance with BNBC and IEC 62305, including air terminals, down conductors, bonding, surge protection devices (SPDs), dedicated earthing network, and testing. The design shall be supported by calculations and drawings submitted during the detailed design stage. |  | Lot
13 | Monitoring system (data logger, communication, web portal and app) |  | Lot
14 | Energy meter(s) |  | Pcs
15 | Installation works, civil/structural works, labelling and signage |  | Lot
16 | Testing, commissioning and Final Acceptance Test (IEC 62446-1) |  | Job
17 | Training, O&M manual, SoP, as-built drawings and handover documents |  | Job
18 | Critical spare parts held in Bangladesh for the DLP (Annex D, Section 7) |  | Lot
19 | Defect Liability Period services – 12 months incl. quarterly preventive maintenance |  | Lot
# | [[[[Add additional Items if required]]]]
# | [[[[Add additional Items if required]]]]
# | [[[[Add additional Items if required]]]]
Add any further items required by your design in the additional rows; leave blank rows that do not apply, but do not change the structure. All equipment and labour needed to complete the works are deemed included.
Quantities and specifications must match your single line diagram, energy simulation and Technical Specification Format (Annex D).
NOTE: SUBMIT THIS BoQ WITH YOUR TECHNICAL OFFER. IT MUST NOT CONTAIN ANY PRICE INFORMATION. Prices go only in the Financial Offer Form (Annex E).
DATE: ______________________________
NAME OF AUTHORISED COMPANY REPRESENTATIVE: ______________________________
SIGNATURE / STAMP OF THE COMPANY: ______________________________

## B2 Lot 2 - Camp 13
BGD-UNHCR RFP 3830 Technical Bill of Quantities (no prices) – Lot 2 – RHEC Camp 13 Design, BoQ, Supply, Installation, Testing and Commissioning of Solar PV Hybrid Power Systems – Two RHECs, Cox’s Bazar
Annex B2 – Technical BoQ
SL | Item | Specification offered (make, model, key ratings) | Unit | Qty | Country of origin | Stock availability / lead time
1 | Solar PV modules – Monocrystalline N-Type or better/advanced technology, minimum 550 Wp per module, with total installed capacity meeting the design requirements (minimum 25 kWp). The stated specification shall be considered the minimum acceptable standard. |  | Pcs
2 | Mounting structure incl. roof fixing and any structural strengthening |  | Lot
3 | DC combiner / PV junction boxes with isolators, gPV fuses and SPDs |  | Set
4 | PV (DC) cables and MC4 connectors |  | Meter
5 | Three-phase hybrid inverter configuration with minimum combined inverter capacity of 20 kW. Bidders may propose one or multiple inverter units to achieve the required capacity and redundancy requirements. |  | Set
6 | LiFePO₄ battery energy storage system incl. BMS, racks/cabinet (≥ 150 kWh gross / ≥ 105 kWh usable) |  | Set
7 | Battery area works: enclosure/ventilation, smoke & heat detection with alarm |  | Lot
8 | Fire extinguishers, Class C (CO₂ / clean agent) |  | Pcs
9 | AC distribution board, automatic changeover/ATS, breakers and integration with existing MDB |  | Set
10 | AC cables incl. trenching / conduit |  | Meter
11 | Earthing system (array, inverter, BESS, boards) - Complete earthing system for solar array, inverter, battery energy storage system (BESS), distribution boards and all associated metallic structures. Design, installation and testing shall comply with the latest edition of BNBC and applicable IEC standards. Earthing bore depth shall be not less than 40 ft (12 m), subject to achieving the required earth resistance value. |  | Lot
12 | Lightning protection system - Complete lightning protection system designed and installed in accordance with BNBC and IEC 62305, including air terminals, down conductors, bonding, surge protection devices (SPDs), dedicated earthing network, and testing. The design shall be supported by calculations and drawings submitted during the detailed design stage. |  | Lot
13 | Monitoring system (data logger, communication, web portal and app) |  | Lot
14 | Energy meter(s) |  | Pcs
15 | Installation works, civil/structural works, labelling and signage |  | Lot
16 | Testing, commissioning and Final Acceptance Test (IEC 62446-1) |  | Job
17 | Training, O&M manual, SoP, as-built drawings and handover documents |  | Job
18 | Critical spare parts held in Bangladesh for the DLP (Annex D, Section 7) |  | Lot
19 | Defect Liability Period services – 12 months incl. quarterly preventive maintenance |  | Lot
# | [[[[Add additional Items if required]]]]
# | [[[[Add additional Items if required]]]]
# | [[[[Add additional Items if required]]]]
Add any further items required by your design in the additional rows; leave blank rows that do not apply, but do not change the structure. All equipment and labour needed to complete the works are deemed included.
Quantities and specifications must match your single line diagram, energy simulation and Technical Specification Format (Annex D).
NOTE: SUBMIT THIS BoQ WITH YOUR TECHNICAL OFFER. IT MUST NOT CONTAIN ANY PRICE INFORMATION. Prices go only in the Financial Offer Form (Annex E).
DATE: ______________________________
NAME OF AUTHORISED COMPANY REPRESENTATIVE: ______________________________
SIGNATURE / STAMP OF THE COMPANY: ______________________________