ANNEX A TERMS OF REFERENCE (ToR)

BGD-UNHCR RFP 3830

FOR THE DESIGN, BoQ, SUPPLY, INSTALLATION, TESTING

AND COMMISSIONING OF SOLAR PV HYBRID POWER SYSTEMS FOR

TWO REFUGEE HIGHER EDUCATION CENTRES (RHECs), COX’S BAZAR – LOT 1: CAMP 4; LOT 2: CAMP 13

1.	BACKGROUND

UNHCR Bangladesh is implementing several higher education access programmes for refugees, including the Refugee Higher Education Access Programme (RHEAP), online certified courses and undergraduate degrees in collaboration with universities. To deliver these programmes, two Refugee Higher Education Centers (RHECs) are being established in the Rohingya refugee camps in Cox’s Bazar: one in Camp 4 (construction nearly complete) and one in Camp 13 (site selected; construction starting). Each center comprises four classrooms, a training room, an office, a library and four toilets.

Reliable electricity is essential for the digital learning model of the centers (laptops/tablets, projectors, Wi-Fi, lighting and fans). UNHCR therefore intends to install a turnkey Solar PV Hybrid Power System (solar PV with lithium iron phosphate battery storage) at each center in order to:

- ensure reliable power during class hours and protect learning time from grid outages;

- reduce operating costs and dependence on diesel generation;

- reduce greenhouse-gas emissions in line with UNHCR’s climate action commitments; and

- provide a durable, low-maintenance system suited to the hot, humid, saline and cyclone-prone coastal environment of Cox’s Bazar.

2.	OBJECTIVE

The objective of this assignment is the design, BoQ, supply, delivery, installation, testing, commissioning, training and handover, on a turnkey basis, of a complete Solar PV Hybrid Power System at each RHEC, including all associated electrical, structural, protection, monitoring and battery storage components, followed by defect-liability and after-sales support, so that each center can operate its full connected load reliably throughout the school day.

3.	PROJECT LOCATION AND LOTS

The requirement is divided into two lots. Bidders may bid for one or both lots. Each lot will be evaluated and awarded separately, and the requirements of this ToR apply to each lot unless stated otherwise. Both centers use the same building design and load profile.

| Lot | Site | Status | Site visit | Start of works |
| --- | --- | --- | --- | --- |
| Lot 1 | RHEC, Camp 4, Cox’s Bazar | Construction nearly complete | Mandatory (proof of visit required) | Contract signature |
| Lot 2 | RHEC, Camp 13, Cox’s Bazar | Building under construction | Strongly recomended (site/plot only) | UNHCR written Notice to Proceed (NTP) |

Site visit: Participation in the site visit to Camp 4 (Lot 1) is mandatory; bids for Lot 1 without proof of site visit will not be considered. Proof of site visit is the UNHCR site-visit attendance register, signed on the day by each bidder’s representative(s) and the UNHCR focal point; UNHCR will verify attendance against this register. For Lot 2, bidders who do not visit the plot shall be deemed to have fully familiarized themselves with site conditions and shall not be entitled to additional claims arising from site conditions after award. Camp access is subject to Government of Bangladesh (RRRC/CiC) permission, which UNHCR will arrange for registered representatives.

Lot 2 – Notice to Proceed: works under Lot 2 shall commence only upon UNHCR’s written NTP, issued once the Camp 13 building is ready for installation. All Lot 2 periods in this ToR run from the date of the NTP. Lot 2 prices shall remain firm until completion of Lot 2 works. If the NTP is not issued within six (6) months of contract signature, either party may request a price review, or UNHCR may cancel the Lot 2 contract without liability to either party.

The structural design of the RHEC building is provided in Annex C to the RFP for reference. The contractor shall verify all dimensions, roof and structural conditions and cable routes on site during the site visit and site assessment.

4.	SCOPE OF WORKS

The contractor shall deliver a complete, fully functional and safe system for each lot. The scope includes, but is not limited to:

- site survey and Site Assessment Report (roof/structural condition, available area, shading, cable routes, existing power sources and distribution board);

- detailed engineering design, Bill of Quantities (BoQ), energy simulation, drawings and calculations, submitted for UNHCR approval;

- supply and delivery to site of all equipment, materials and consumables (PV modules, hybrid inverter(s), battery energy storage system (BESS), mounting structure, DC/AC distribution and protection, cables, earthing, lightning protection, monitoring, fire safety equipment, labels and signage);

- civil and structural works required for the installation (mounting, strengthening, cable trenches/ducts, battery room/enclosure works);

- installation, integration with the centre’s electrical distribution board and with any existing grid/generator supply;

- testing, commissioning, Final Acceptance Test and handover with as-built documentation;

- training of UNHCR staff, partner staff and facility operators; and

- warranty management, Defect Liability Period (DLP) services (12 months from Final Acceptance; see Section 10) and after-sales support.

The contract price for each lot is a lump sum. Lightning protection, earthing, surge protection, fire detection/suppression for the battery area, cabling, and any structural strengthening identified during design are part of the scope and are deemed included in the lump sum. No variation will be accepted for items that are necessary for a complete, safe, and code-compliant system.

4.1	UNHCR approval gates (linked to payment milestones, Section 14)

- Site Assessment Report – within 10 calendar days of contract signature (Lot 1) or NTP (Lot 2);

- Detailed Engineering Design package, including the final detailed BoQ – UNHCR reviews within 7 working days of receipt of a complete package; no major equipment may be ordered before design approval;

- Inspection of major equipment on delivery to site (make, model and serial numbers against the approved design and the bid);

- Witnessed Testing & Commissioning and Final Acceptance Test before handover.

5.	DESIGN BASIS

5.1	Connected load (each centre)

| Equipment | Quantity | Unit wattage (W) | Connected load (W) | Daily energy (Wh/day, 8 h) |
| --- | --- | --- | --- | --- |
| Laptops / tablets | 120 | 60 | 7,200 | 57,600 |
| Multimedia projectors | 5 | 300 | 1,500 | 12,000 |
| Ceiling fans | 24 | 75 | 1,800 | 14,400 |
| LED lights | 25 | 15 | 375 | 3,000 |
| Wi-Fi routers | 3 | 15 | 45 | 360 |
| Total |  |  | 10,920 | 87,360 |

5.2	Design parameters (minimum)

| Parameter | Requirement |
| --- | --- |
| Peak connected load | Approximately 11 kW |
| Daily energy demand | Approximately 87 kWh/day |
| Design energy demand | Minimum 100 kWh/day |
| Battery backup (autonomy) | Minimum 8 hours of full connected load without solar input |
| PV array | Minimum 25 kWp |
| Hybrid inverter capacity | Minimum 20 kW (three-phase); higher capacity or multiple units permitted with design justification |
| Battery technology / capacity | LiFePO₄; minimum 150 kWh gross, minimum 105 kWh usable |
| System design life | Minimum 15 years |

5.3	System configuration and operating logic

Solar PV Hybrid: solar PV with battery storage is the primary source. The system shall be designed for off-grid operation, with provision for integration with the national grid and/or generator (existing or future) through an automatic transfer/changeover arrangement with the following priority: (1) solar PV supplying loads and charging the BESS; (2) BESS; (3) grid; (4) generator. The BESS should also be chargeable from grid/generator when solar is insufficient. The contractor shall assess the available power sources during the site survey and propose a control strategy in the design.

5.4	Design data and simulation

The design shall be based on the average annual solar irradiation of the site. Bidders shall submit an energy simulation using recognized software (PVsyst, HOMER or equivalent) and state the irradiation dataset used (e.g. Global Solar Atlas/Solargis, PVGIS, NASA POWER or Meteonorm). The simulation shall show monthly and annual energy yield, system losses, performance ratio, battery state-of-charge profile and the ability to meet the design energy demand and the 8-hour autonomy. The same assumptions shall be used consistently in the BoQ, single line diagram (SLD) and datasheets.

6.	MINIMUM TECHNICAL REQUIREMENTS

The minimum requirements below are mandatory. Detailed parameters are listed in the Technical Specification Format (Annex D), which bidders shall complete for every major component. Bidders may offer higher specifications.

6.1	Solar PV modules

| Parameter | Minimum requirement |
| --- | --- |
| Technology | Monocrystalline N-type (TOPCon or equivalent/higher); polycrystalline not accepted |
| Module efficiency | ≥ 22% |
| Degradation | ≤ 1% in year 1; ≤ 0.4% per year thereafter |
| Junction box / connector | IP68 with bypass diodes / MC4-compatible |
| Frame / glass | Anodised aluminium / tempered, anti-reflective, PID-resistant (IEC 62804) |
| Certification | IEC 61215, IEC 61730-1/-2, IEC 61701 (salt mist – mandatory), IEC 62716; ISO 9001 manufacturer |
| Manufacturer | Listed on the BloombergNEF Tier-1 PV module list (latest quarter) – evidence required |
| Warranty | Product ≥ 12 years; performance ≥ 25 years |

6.2	Hybrid inverter

| Parameter | Minimum requirement |
| --- | --- |
| Type / capacity | Three-phase hybrid (PV + battery + grid/generator), minimum 20 kW total |
| Efficiency / MPPT | Maximum efficiency ≥ 98%; minimum 2 independent MPPTs |
| Protection / IP | Over/under voltage, overcurrent, short circuit, ground fault, anti-islanding, surge; IP65 (or installed in IP65 enclosure) |
| Communication | RS485/CAN/Ethernet/Wi-Fi; compatible with offered BESS and monitoring |
| Certification | IEC 62109-1/-2, IEC 61000 (EMC), IEC 61727 and IEC 62116 (if grid-connected) |
| Warranty | Minimum 5 years |

6.3	Battery Energy Storage System (BESS)

| Parameter | Minimum requirement |
| --- | --- |
| Chemistry | Lithium iron phosphate (LiFePO₄) |
| Capacity | ≥ 150 kWh gross; ≥ 105 kWh usable |
| Usable depth of discharge | ≥ 70% (as used in the design) |
| Cycle life / design life | ≥ 6,000 cycles; ≥ 15 years |
| BMS | Integrated smart BMS (over/under voltage, overcurrent, short circuit, temperature, cell balancing) |
| Enclosure | Minimum IP54; rack or cabinet; fire-retardant materials |
| Certification | IEC 62619, UN 38.3, IEC 61000 (EMC), UL 1973 or equivalent; UL 9540A thermal-runaway test report (or equivalent) |
| Warranty | Minimum 10 years (or equivalent cycle/throughput warranty) |

The BESS will be installed in an occupied education building. A UL 9540A (or equivalent) thermal-runaway test report for the offered battery is required to demonstrate that a cell failure does not propagate to fire.

6.4	Mounting structure

| Parameter | Minimum requirement |
| --- | --- |
| Material | Hot-dip galvanized steel (zinc ≥ 80 µm, ISO 1461) or anodized aluminium; SS304 fasteners; anti-theft bolts |
| Wind load | Designed in compliance with the latest edition of BNBC and all applicable standards; wind loading calculations based on the BNBC-designated wind speed for the project location |
| Design / documentation | Structural calculation and drawings signed by a qualified structural engineer; roof attachment without compromising waterproofing |
| Design life | ≥ 25 years |

Mounting design shall comply with the Bangladesh National Building Code (BNBC 2020) wind-load provisions for Cox’s Bazar. The roof load check and mounting design shall be based on the structural design of the RHEC building (Annex C to the RFP), verified on site (see Annex F, criterion 5, requirement 12).

6.5	Balance of system, protection and safety

- Cables: PV cables to IEC 62930/EN 50618; AC cables to IEC 60502; UV/salt-mist resistant; voltage drop ≤ 3% (DC) and ≤ 3% (AC) under design current; underground or conduit routing protected against damage;

- DC/AC distribution boards and combiner boxes: IP65, with DC isolators, MCB/MCCB/fuses (IEC 60947, IEC 60269-6 gPV), labelled and coordinated;

- Surge protection: Type II SPDs on DC and AC sides (Type I+II at the main board if an external lightning protection system is installed);

- Earthing: copper-bonded earthing for array, inverter, BESS and boards; earth resistance ≤ 5 Ω (maximum 10 Ω in the dry season), tested with a calibrated earth tester;

- Lightning protection: risk assessment and protection system to IEC 62305 for the array and building;

- Fire safety for the battery area: smoke and heat detection with audible/visual alarm, Class C (CO₂/clean agent) extinguishers inside and outside, ventilation as required by the BESS manufacturer, signage and emergency shutdown;

- Monitoring: web portal and mobile app with real-time and historical data (PV, load, BESS SoC, grid/generator), alarms and remote access; read-only access for UNHCR during and after the DLP.

Compliance with Bangladesh import standards: imported PV modules, inverters, charge controllers and batteries shall meet the standards set by SREDA and enforced by BSTI (modules IEC 61215/IEC 60904; inverters IEC 62109; charge controllers IEC 62509; batteries IEC 61427/IEC 62619). Bidders shall confirm compliance and that equipment can be cleared without delay.

7.	TESTING, COMMISSIONING AND ACCEPTANCE

Testing and commissioning shall follow IEC 62446-1 and be witnessed by UNHCR. As a minimum:

- visual and mechanical inspection, continuity, polarity, insulation resistance and earth resistance tests;

- PV string open-circuit voltage and short-circuit/operating current tests (I-V curve where available);

- inverter, BESS and protection functional tests, including grid/generator changeover and emergency shutdown;

- battery commissioning report and capacity verification;

- monitoring system functional test with UNHCR access;

- minimum 3 consecutive days of operation without major faults, with the performance ratio (IEC 61724-1) compared to the design simulation.

Final Acceptance is issued by UNHCR after successful tests, training and receipt of the handover documents. Final Acceptance (equivalent to substantial completion under the GCC for Civil Works) starts the 12-month Defect Liability Period.

8.	TRAINING

The contractor shall deliver hands-on training at each site for UNHCR staff, partner staff and facility operators (minimum 1 day per site, maximum 10 participants per session), covering: system overview and energy flow; daily operation and monitoring; routine maintenance (module cleaning, battery and inverter checks); troubleshooting and fault codes; safety, fire response and emergency shutdown; and record keeping. Training materials, a simple SoP in English and Bangla, and a refresher session six (6) months after handover shall be provided.

9.	DOCUMENTATION AND DELIVERABLES

| Stage | Deliverables |
| --- | --- |
| With the bid (technical offer) | Preliminary design and energy simulation; preliminary SLD; load and battery autonomy calculation; Technical BoQ without prices (Annex B); completed Technical Specification Format (Annex D); datasheets and certificates; manufacturer authorisation letters; warranty statements; work plan (Gantt); key personnel CVs (Annex J); equipment/tools list |
| Design stage | Site Assessment Report; detailed design report; final detailed BoQ (quantities may be refined but the lump-sum price per lot does not change); final SLD and string layout; structural calculations and drawings; cable, breaker and protection sizing; earthing and lightning protection design; battery area layout and fire safety plan; HSE plan; project schedule |
| During installation | Weekly progress reports with photos; material inspection records |
| Handover | As-built drawings (PDF and CAD); test and commissioning reports (IEC 62446-1); O&M manual; SoP (English/Bangla); warranty certificates registered in UNHCR’s name; asset register with serial numbers; spare parts list; training records |

10.	WARRANTY, DEFECT LIABILITY AND AFTER-SALES SUPPORT

| Component | Minimum warranty |
| --- | --- |
| PV modules | 12 years product; 25 years performance |
| Hybrid inverter | 5 years |
| Battery system | 10 years |
| Installation workmanship | 24 months from Final Acceptance |
| Other BOS components | 2 years |

Defect Liability Period (DLP): 12 months from Final Acceptance. During the DLP the contractor shall acknowledge a fault report within 24 hours, attend site within 3 working days, and rectify the defect within 7 calendar days. Where a major component must be replaced under warranty, the replacement shall be installed within 15 calendar days; if longer, the contractor shall provide a temporary substitute so that the centre remains operational.

The contractor shall keep in Bangladesh a stock of critical spares for the duration of the DLP (at minimum: inverter communication/control card or one spare inverter module where modular, battery modules or cells equivalent to 5% of capacity, fuses, breakers, SPD cartridges, MC4 connectors) and shall carry out one preventive maintenance visit per quarter during the DLP.

The contractor shall take back and recycle, in line with national regulations, any batteries or electronic components replaced during the warranty period.

11.	HEALTH, SAFETY, ENVIRONMENT AND CODE OF CONDUCT

- submit a site-specific HSE plan before mobilisation; use PPE at all times; apply working-at-height and electrical isolation (lock-out/tag-out) procedures;

- battery fire and thermal event response measures during installation and operation;

- comply with RRRC/CiC camp access rules, working hours and security instructions; keep the site safe for students and staff;

- collect and dispose of packaging and waste responsibly and restore any damaged site elements;

- All personnel shall comply with the UN Supplier Code of Conduct (Annex K) and UNHCR requirements on the Prevention of Sexual Exploitation and Abuse (PSEA) and child safeguarding.

12.	WORK PLAN AND TIMELINE

The work for each lot shall be completed within 90 calendar days from contract signature (Lot 1) or from the NTP (Lot 2). Bidders shall submit a Gantt chart with resources and dependencies. Indicative milestones:

| Milestone | Indicative timing (calendar days) |
| --- | --- |
| Site Assessment Report submitted | Day 10 |
| Detailed design approved by UNHCR | Day 25 |
| Major equipment delivered and inspected | Day 60 |
| Installation completed | Day 80 |
| Testing, commissioning, training and handover | Day 90 |

Where one contractor is awarded both lots, the lots may be executed in parallel; no extension will be granted on that ground unless site access or operational constraints are imposed by UNHCR.

13.	KEY PERSONNEL

| Position | Minimum qualification and experience |
| --- | --- |
| Project Manager (1) | B.Sc. in Engineering (Electrical/EEE or relevant); minimum 8 years’ experience, including management of at least 3 solar PV projects ≥ 20 kWp |
| Electrical / Solar Design Engineer (2) | B.Sc. in EEE or Renewable Energy; minimum 5 years’ experience in design, installation, testing and commissioning of solar PV systems. Battery storage experience is accepted from any member of the key team (Project Manager or either engineer), evidenced by either involvement in at least one completed solar project with battery storage (any size or chemistry) or a manufacturer training/installer certificate for the offered hybrid inverter or battery system |
| Site Supervisor (1) | Diploma in Electrical Engineering or equivalent; minimum 3 years supervising solar/electrical installations; valid electrical supervisor licence (BERC/Licensing Board) |

CVs shall be submitted using Annex J with copies of degrees and licences. Key personnel may not be replaced without UNHCR’s prior written approval of a person with equal or better qualifications.

14.	PAYMENT TERMS, RETENTION AND LIQUIDATED DAMAGES

No advance payment will be made. Payments per lot are made by bank transfer net 30 days after UNHCR’s acceptance of each milestone and receipt of a correct invoice:

| Milestone | Payment |
| --- | --- |
| Approval of the Site Assessment Report and Detailed Engineering Design | 20% |
| Delivery of major equipment to site, following UNHCR inspection | 40% |
| Installation completed, verified by UNHCR | 20% |
| Testing & commissioning, Final Acceptance, training and handover documents | 20% |
| Retention: 10% is withheld from each milestone payment above and released within 30 days of the Certificate of Final Completion, issued on expiry of the 12-month DLP and rectification of all notified defects | 10% of each payment |

Performance security: no separate performance security (bank guarantee) is required. The 10% retention secures performance and the rectification of defects, as provided in the Construction Services Contract (Annex N to the RFP).

Liquidated damages: if the contractor fails to complete the works within the contractual period, UNHCR may deduct liquidated damages of 0.1% of the lot contract value per calendar day of delay, up to a maximum of 10% of the lot contract value, without prejudice to UNHCR’s other remedies under the Construction Services Contract and the General Conditions of Contract for Civil Works (Annex I to the RFP).

15.	BIDDER QUALIFICATION AND EVALUATION

Pre-qualification (pass/fail), technical scoring and financial evaluation are set out in Section 2.5 of the RFP and in the Technical Evaluation Scoring Matrix (Annex F). In summary, bidders must have a valid trade licence, VAT and TIN registration, minimum three (3) years in solar PV implementation, at least three (3) completed solar PV projects of ≥ 20 kWp, financial capacity of BDT 5,000,000 per lot bid (BDT 10,000,000 for both lots), proof of site visit (Lot 1), Tier-1 PV modules, mandatory product certifications, signed acknowledgement of the GCC for Civil Works and the UN Supplier Code of Conduct, a signed Bidder’s Undertaking (Annex L) and a bid security (Annex G).

End of ToR