## ALL BLD (ELEC)
Annex C Financial Offer form
Sl No. | Description of Item | Unit of Measurement | Qty | Supply in (unit price BDT) | Installation in (BDT) | Total Amount in (BDT)
1 | WIRING CABLE (BYM/ NYY-XLPE) (Supply only): Cable with following PVC insulated and sheathed stranded cable (BYM/ NYY) & PVC insulated Green / Yellow bi- coloured ECC wire (BYA). Cables shall be manufactured and tested according to IEC / BS / VDE standards along with relevant BDS standard as per detailed specification . The work shall be carried out as per direction & approval of the Engineer In Charge. Cable manufacturer(s) must have valid type test certificate (within last seven years) from internationally accredited laboratory (like CPRI, KEMA etc.) accepted / approved by the Engineer In Charge. |  | 2
1.1 | 1C-2x1.5sqmm (BYA) FRLS cable. | Meter | 1000 |  | N/A | 0
1.2 | 1C-2x2.5sqmm (BYA) FRLS cable. | Meter | 710 |  | N/A | 0
1.3 | 1C-2x4 sqmm (BYA) FRLS cable. | Meter | 50 |  | N/A | 0
1.4 | 3C-1x6.0 sqmm (BYM) FRLS cable. | Meter | 350 |  | N/A | 0
1.5 | 1X-4Cx25sqmm (NYY/XLPE) with 16 sqmm (BYA) ECC wire | Meter | 120 |  | N/A | 0
2 | PVC PIPE (Supply only): Supply of approved quality heavy-duty PVC conduit/pipe of specified size complete with all associated conduit fittings and accessories, including junction boxes, circular boxes, outlet boxes, pull boxes, covers, couplers, bends, adaptors, saddles, and other necessary materials, delivered to site complete in all respects. Installation and cable works are excluded.
2.1 | Minimum inner Dia. 25 mm & minimum wall thickness 1.5 mm. for above Cable Items (Cable Items No- 1.1-1.4) | Meter | 2000 |  | N/A | 0
2.2 | Minimum inner dia 50 mm & minimum wall thickness 2.2 mm. for above Cable Items (Cable Items No- 1.1-1.4) | Meter | 120 |  | N/A | 0
2.3 | Minimum inner dia 50 mm & minimum wall thickness 2.2 mm. for above Cable Items-1.5 | Meter | 120 |  | N/A | 0
3 | Installation of Heavy-Duty PVC Conduit with Cable and Accessories (Installation Only): Installation of approved quality heavy-duty PVC conduit of specified size complete with all fittings, junction/pull boxes, supports, fixing accessories, chasing, cutting, embedding, and testing for clear cable passage, as per drawings and Engineer's instructions. The conduits shall be securely tied to reinforcement steel bars at 900 mm intervals using 20/24 SWG GI wire to prevent displacement during concreting. The rate shall include all accessories, fixing materials, tracing and cutting out outlet locations after removal of shuttering, cleaning of outlets, and making good all damages to civil and architectural finishes resulting from the installation work, as directed by the Engineer. Scope includes conduit installation only.
3.1 | Minimum inner Dia. 25 mm & minimum wall thickness 1.5 mm. for above Cable Items for (Cable Items No- 1.1-1.4) | Meter | 2000 | N/A |  | 0
3.2 | Minimum inner dia 50 mm & minimum wall thickness 2.2 mm. for above Cable Items for (Cable Items No- 1.1-1.4) | Meter | 120 | N/A |  | 0
3.3 | Minimum inner dia 50 mm & minimum wall thickness 2.2 mm. for above Cable Items-1.5 (1X-4Cx25sqmm (NYY/XLPE) with 16 sqmm (BYA) ECC wire) | Meter | 120 | N/A |  | 0
4 | CEILING FAN: Supplying & fixing AC capacitor type ceiling fan (without regulator) of following specifications and sizes complete with minimum 305 mm (1 ft) long and 0.75 -1.0" dia, 2.3 mm thickness MS pipe down rod, tempered cast aluminum blades, 2.5 µf 230V AC capacitor, canopy, double Z ball bearing, best quality silicon sheet core, best quality copper made super enamel wire, aluminum alloyed casting body / metal body having safety pin with powder coated heat / docu paint as required as per BDS 818 etc. connecting PVC wire complete as required. Rated voltage : 230 volts Rated frequency : 50 Hz Rated speed : 300 rpm ± 5 % Service value : Minimum 3.5 m3 / min / watt Temperature rise : Maximum 55ºC Class of Insulation : Minimum E Noise level : Maximum 60 dB at a distance of 1 meter. |  |  |  |  | 0
4.1 | 1400mm.(56") sweep (Input power: Maximum 65 watt.) | each | 37 |  |  | 0
5 | EXHAUST FAN: Providing and fixing of following propeller fan AC capacitor type wall mounted exhaust fan complete with blade, steel frame standard wall louver shutter, PVC insulated connecting wire etc. complete as required including cutting wall and mending good the damages as per direction of the Engineer.
5.1 | 10" Exhaust fan plastic body (foreign made accepted / approved by the Engineer). | each | 5 |  |  | 0
6 | HEAVY DUTY INDUSTRIAL EXHAUST FAN: Supply and installation of Wall mounted heavy duty industrial exhaust fan: Type 230V, 50 Hz, complete with stainless steel blade, steel frame, standard wall louver shutter with necessary accessories (specially used for kitchen of hospital, student hostel / hall, prison cell, barrack, large auditorium etc). |  |  |  |  | 0
6.1 | 24" | each | 2 |  |  | 0
7 | TUBE LIGHT FITTINGS (LED): Supply & fixing LED tube light fittings of following specifications: Luminous efficacy: 100 lm/W(minimum) Power Factor: minimum 0.95 Colour Rendering Index(Ra) : i) For Residential building Ra≥80 ii) For office and other types of buildings 70≤Ra<85 Driver : As per IEC,UL, CE, ISO standard, LED chips :As per IEC,UL, CE, ISO standard, Colour temperature : 3500K-6500K (Warm-White) Model & sample to be accepted / approved by the Engineer-in-charge (with 1 years warranty). |  |  |  |  | 0
7.1 | Watt-36 x 4' | each | 65 |  |  | 0
8 | WALL LIGHT FITTINGS (LED): Supply & fixing LED tube light fittings of following specifications: Luminous efficacy: 100 lm/W(minimum) Power Factor: minimum 0.95 Colour Rendering Index(Ra) : i) For Residential building Ra≥80 ii) For office and other types of buildings 70≤Ra<85 Driver : As per IEC,UL, CE, ISO standard, LED chips :As per IEC,UL, CE, ISO standard, Colour temperature : 3500K-6500K (Warm-White) Model & sample to be accepted / approved by the Engineer-in-charge (with 1 years warranty). |  |  |  |  | 0
8.1 | Watt-25 | each | 12 |  |  | 0
9 | EMERGENCY STAIR EXIT LIGHT(LED): Supply and installation of ceiling mount emergency "Exit light" complete with rechargeable battery and charge light and other necessary accessories suitable for AC / DC power supply (230V single phase) as per NFPA 101 | each | 8 |  |  | 0
10 | LED SIGN : Supply & fixing of LED sign of the following features and model with all necessary elements such as drivers, chips etc. complete model and sample shall be approved by the Engineer. |  |  |  |  | 0
10.1 | 3W Exit Light | each | 14 |  |  | 0
11 | FLOOD LIGHT FITTINGS (LED NARROW BEAM) (FOR OUTER ILLUMINATION): Supply & fixing LED narrow beam flood light fittings of following specifications: Luminous efficacy: 100lm/w(minimum), Power Factor: minimum 0.95 Colour Rendering Index(Ra) :70≤Ra<85 Driver: As per IEC,UL, CE, ISO standard, Ingress Protection:IP 67 LED chips As per IEC,UL, CE, ISO standard, Colour temperature : 3500K-6500K (Warm-White) Model & sample to be accepted / approved by the Engineer-in-charge (with 1 years warranty). |  |  |  |  | 0
11.1 | Narrow Beam Long Distance Throw , 100W LED Spotlights (IP-67) | each | 2 |  |  | 0
12 | FOUNTAIN LIGHT JUNCTION BOX: Supply & Fixing of fountain light junction box of the following sizes as per sample accepted / approved by the Engineer-in-charge (with 1 years warranty) |  |  |  |  | 0
12.1 | 4 way | each | 150 |  |  | 0
13 | GALVANIZED CABLE TRAY WITH COVER : Supply, fitting and fixing galvanized cable tray made of 18 SWG (1.2 mm) MS Sheet evenly perforated with 7 mm width Capsule hole punch with self-Hanging Facility at top, joint clamp,top cover including fabricating cost of electricity, tools and plants, workshop charges, carriage of the same, cutting groves in the RCC or brick work, mending good the damages with CC (1:2:4), etc. complete for all floors accepted by the engineer. |  |  |  |  | 0
13.1 | 100x50 mm with cover | Meter | 192 |  |  | 0
14 | DISTRIBUTION BOARD: Supplying and fixing of almirah type 18 SWG metal board of depth 228mm (6") duly painted with powder coating with epoxy polyester resin on all surfaces of board (gray / off-white) having built in push type / suitable locking arrangement including metal bridges of suitable size for fixing of all electrical control devices complete with suitable anchoring arrangement in wall / column and keeping provision for cable inlets and exits as required (only front surface of the board will be considered for measurement accepted/approved by the Engineer-incharge. |  |  |  |  | 0
14.1 | SDB | each | 5 |  |  | 0
| Incoming: |  |  |  |  | 0
| 1 Set - 230V, 32 amps. DP&NE hard drawn electrolytic copper busbar |  |  |  |  | 0
| 1 No- 32A, 10KA, 230V, DP MCB |  |  |  |  | 0
| Outgoing: |  |  |  |  | 0
| 10 Nos- 10A, 10 kA, SP Miniature Circuit Breaker(MCB). |  |  |  |  | 0
0
14.2 | SDB PUMP | each | 1 |  |  | 0
| Incoming: |  |  |  |  | 0
| 1 Set - 230V, 32 amps. DP&NE hard drawn electrolytic copper busbar |  |  |  |  | 0
| 1 No- 32A, 10KA, 230V, DP MCB |  |  |  |  | 0
| Outgoing: |  |  |  |  | 0
| 5 Nos- 20A, 10 kA, DP Miniature Circuit Breaker(MCB). |  |  |  |  | 0
15 | MDB- | Each | 1 |  |  | 0
| INCOMING : 2 Set- 420V, 50A (20KA), adjustable type TP MCCB . & NE hard drawn electrolytic copper bus bar. With Mechanical interlock 1 Nos. - 420V, 50 / 5 ratio current transformer with suitable accuracy & burden. OUTGOING : 9 Nos.- 230V, 32A (10 KA) DP MCB 1 Nos.- 420V, 32A (10 KA) TP MCB |  |  |  |  | 0
| Rming System: |  |  |  |  | 0
| 3 Nos 500/5A CT |  |  |  |  | 0
| 1 Set - Control Fuse |  |  |  |  | 0
| 1 Set- Indicating Lamp (RYB) |  |  |  |  | 0
| 1 No- Digital MultiRm |  |  |  |  | 0
16 | ATS | Each | 3 |  |  | 0
| INCOMING : 2 No.- 420V, 50A (20KA), TP MC 1 Nos. - 230V, 50 / 5 ratio current transformer with suitable accuracy & burden. OUTGOING : 1 Set- 420V, 4P 50A Connector |  |  |  |  | 0
| Rming System: |  |  |  |  | 0
| 2 Set - Control Fuse |  |  |  |  | 0
| 1 Set- Indicating Lamp (RYB) |  |  |  |  | 0
| 1 Set-Timer Relay |  |  |  |  | 0
17 | UNIVERSAL COMBINED SWITCH SOCKET OUTLETS: Providing & fixing 230 volt single phase universal combined switch socket outlet (surface / concealed type) Manufactured/ Assembled and tested in accordance with IEC / VDE / NEMA / BS / JIS along with relevant BDS IEC standards mounted on required size 18 SWG galvanized plain sheet board / plastic board (self-extinguishing 650 degree centigrade) of 76.2 mm. (3") depth. Sample to be approved by the Engineer-incharge. Manufacturer shall have certificate of standard which they follow. |  |  |  |  | 0
17.1 | 13/15/16 / 20 Amps | each | 67 |  |  | 0
18 | GANG SWITCH: Providing & fixing 230 volts.5 / 6 amps (minimum) concealed type following switch / switch socket Manufactured / Assembled and tested in accordance with IEC / VDE / NEMA / BS / JIS along with relevant BDS IEC standards mounted on required size 18 SWG galvanized plain sheet / PVC board (Self.extinguishing 650 Degree Centigrade) of 76.2 mm (3'') depth .All electrical contacts shall be of brass / copper. |  |  |  |  | 0
18.1 | Four gang switch | each | 30 |  |  | 0
18.2 | Three gang switch | each | 3 |  |  | 0
18.3 | Two gang switch | each | 5 |  |  | 0
18.4 | One gang switch | each | 2 |  |  | 0
18.5 | Gang Type Fan Regulator | each | 37 |  |  | 0
19 | LIGHTNING PROTECTION SYSTEM |  |  |  |  | 0
19.1 | AIRTERMINAL | each | 30 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Height: 2'-0" |  |  |  |  | 0
| Diameter: 15mm |  |  |  |  | 0
19.2 | BASE PLATE | each | 30 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Thickness: 4mm |  |  |  |  | 0
| Diameter:6"x6" |  |  |  |  | 0
19.3 | LOOP CONDUCTOR | Meter | 120 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Diameter: 7mm |  |  |  |  | 0
19.4 | DOWN CONDUCTOR | Meter | 120 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Diameter: 7mm |  |  |  |  | 0
19.5 | BONDING CONDUCTOR | Meter | 20 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Diameter: 7mm |  |  |  |  | 0
19.6 | EARTH ELECTRODE | Feet | 480 |  |  | 0
| Materials: Copper |  |  |  |  | 0
| Diameter: 12.7mm |  |  |  |  | 0
19.7 | TEXT BOX | each | 12 |  |  | 0
| Size: 200x200mm |  |  |  |  | 0
19.8 | EARTH PIT | each | 12 |  |  | 0
| Boring depth: 40 ft |  |  |  |  | 0
| Ground Rod dia: 12.7 mm CU |  |  |  |  | 0
20 | EARTHING SYSTEM FOR MDB, SDB |  |  |  |  | 0
20.1 | Supply & Fixing of fan hook as p/ direction of EngineerinCharge. Supply & Installation of Earthing the Electrical Installation with 38.10mm (1.5") diaRm G.I. pipe/Pole (upto 80ft) along with 12.7mm dia Solid Copper Rod, securely bonded with # 1x 0 SWG standard copper wire (ECC) as earth lead required for the earth connection of all the Sub- station Equipment with the earthing block including necessary washer, cable, lug, nuts, bolts etc. The earth electrode will be sunk up to 80'-0'' by tube well sinking method including necessary connections, all complete as required to maintain an earth resistance with in 1 (one) Ohm. If individual earthing resistance does not come greater 1 ohm then client have to install extra earthing or have to bear the cost for additional earthing. | Job | 1 |  |  | 0
20.2 | Earth Bar 25x4mm | Pcs | 1 |  |  | 0
21 | ACCESSORIES |  |  |  |  | 0
i | PVC tape | Pcs | 1000 |  |  | 0
ii | PIB tape | Pcs | 1000 |  |  | 0
iii | 7/8 No. Rawl plug(PVC) | Pcs | 500 |  |  | 0
iv | Rawl Bolt | Pcs | 500 |  |  | 0
v | 1", 1¼", 1 ½" Wood Screw | Pcs | 500 |  |  | 0
vi | 1", 1¼", 1 ½" M.K. Screw | Pcs | 500 |  |  | 0
vii | 14/16 SWG G.I. Wire | Kg | 10 |  |  | 0
viii | Ebonite Sheet (4'x8') | Each | 20 |  |  | 0
ix | Ebonite Sheet round(6") | Each | 20 |  |  | 0
x | Ebonite Sheet round(5") | Each | 20 |  |  | 0
xi | Ebonite Sheet round(4") | Each | 20 |  |  | 0
xvi | Cable tie(6",8",10",12" 100pcs bag) | Bag | 20 |  |  | 0
xvii | Washer | Pcs | 500 |  |  | 0
xviii | 3/4" Single cir. Box(3-way) | Pcs | 200 |  |  | 0
xix | 3/4" Single cir. Box(2-way) | Pcs | 200 |  |  | 0
xx | 3/4" Single cir. Box(1-way) | Pcs | 200 |  |  | 0
xxi | 3/4" Double cir. Box(3-way) | Pcs | 200 |  |  | 0
22 | TAGGING AND IDENTIFICATION FOR ELECTRICAL SYSTEM | Job | 1 |  |  | 0
| Tagging and identification of all equipment like ACB, MCCB, MCB, MDB, DB, SDB, light, cablings, etc. as per IEC guidelines. |  |  |  |  | 0
23 | TESTING & COMMISSIONING FOR ELECTRICAL SYSTEM | Job | 1 | N/A | N/A | 0
| After proper installation and certification the system shall be tested, commissioning and balancing as per direction and recommendation by the Manufacturer as well as per NBC, International Electric Code and Electrical Codes under NFPA. Submit Testing and Commissioning protocols at least 15 days before commissioning for formal approval. All Testing and Commissioning must be done in presence of Electrical Consultant's representative at site. |  |  |  |  | 0
0
| Total for Electrical System |  |  | Total Electrical= |  | 0
Total Amount in words

## FDS-Main Items
Annex C Financial Offer Form
Annex 1.A: Supply of Fire Detection & Alarm System
SL. | Scope of Supply | Unit | Qty. | Supply in (BDT) | Total Amount in (BDT)
1 | Conventional Fire Alarm Control Panel 2 Zone Capacity +1 Conventional NAC: Certification: UL / FM/ AENOR Certified. | Set | 1 |  | 0
2 | Power Supply Unit: 24 VDC @10A Certification: UL / FM/ AENOR Certified. | Nos. | 1 |  | 0
3 | Conventional Manual Call Point / Pull Station : Certification: UL / FM/ AENOR Certified. | Nos. | 6 |  | 0
4 | Conventional Fire Alarm Sounder with Strobe: Certification: UL / FM/ AENOR Certified. | Nos. | 9 |  | 0
5 | Conventional Output / Control Module: Certification: UL / FM/ AENOR Certified. | Nos. | 2 |  | 0
6 | Conventional Fault Isolator Module: Certification: UL / FM/ AENOR Certified. | Nos. | 3 |  | 0
7 | Conventional Smoke Sensor Detector Certification: UL / FM/ AENOR Certified. | Nos. | 24 |  | 0
8 | Conventional Heat Sensor Detector Certification: UL / FM/ AENOR Certified. | Nos. | 1 |  | 0
9 | Fire Alarm Cable: 2 Core x 1.5mm Sq, 300/500V, Solid Core, Red Color Certification: UL Listed. | RM | 300 |  | 0
10 | Fire Alarm Cable: 2 Core x 2.5mm Sq, 300/500V, Solid Core, Red Color Certification: UL Listed. | RM | 200 |  | 0
Sub-Total Amount (Ex- Works) BDT = |  |  |  |  | 0
Annex 1.B: Supply of CO2 & ABC Types Extinguisher
SL. | Scope of Supply | Unit | Qty. | Supply in (BDT) | Total Amount in (BDT)
1 | DRY CHEMICAL POWDER TYPE Supply & fixing of thc following capacities multi purposc ABC dry chemical powder stored pressure type with manometer system fire ertinguisher suitable for repeated use complete with wall bracket. Nitrogen (N2) cartidge. easy refilling system etc. as per sample accepted & approred by the Enginecr in Charge. Mono Ammonium Phosphate (minimum 40%) based ABC dry chemical agent & has a moisture-proof, anti-caking properties.Working pressure : l2 BAR minimum & Test pressure : 25 BAR minimum Proper fire rating (as per NFPA IO/BS/EN) according to the capacity of the extinguisher. Also sample ofthe dry chcmical powder will be testedd by the proper authority in Bangladesh if needed. Capacity : 5 Kg | Set | 11 |  | 0
2 | CARBON-DI-OXIDE TYPE: Supply & fixing of the following capacities multi purposr ABC dry chemical powder manomcter system fire extinguisher suitable for repeated use complete with wall bracket. CO2 cartridge, easy refilling system etc. as per sample acceptcd & approved by the Engineer in Charge. Working pressure : 12 BAR minimum & Tcst pressure : 25 BAR minimum. Proper fire rating (as per NFPA l0 / BS / EN) according to the capacity of the extinguisher. Also sample of the Carbon-di-Oxide will be tested by the proper authority in Bangladesh if needed. Capacity : 5 Kg | Set | 11 |  | 0
Sub-Total Amount (Ex- Works) BDT = |  |  |  |  | 0
Grand Total Combining Both Supply & Insttalation |  |  |  |  | 0

## FDS-Local
Annex C Financial Offer Form
Annex 1.C: Supply of Fire Detection & Alarm System (Local)
SL. | Scope of Supply | Unit | Qty. | Supply in (BDT) | Total Amount in (BDT)
1 | PVC Pipe, Accessories & Other Consumable Materials: | RM | 350 |  | 0
2 | Battery: 1. FACP, (12V 26Ah 2 set) 2. Power Supply unit (12V 7.5Ah 2 set) | Lot | 1 |  | 0
3 | Back Box for Detectors: Local Make. | Nos. | 29 |  | 0
4 | Back Box for Module, MCP, Horn & Horn with Strobe: Local Make. | Nos. | 17 |  | 0
5 | PVC Board Tag Supply for Devices & Others | Lot | 1 |  | 0
Sub-Total Amount BDT = |  |  |  |  | 0
Annex 1.D: Installation, Testing & Commissioning of Fire Detection & Extinguisher (Local)
SL. | Scope of Work | Unit | Qty. | Installation in (BDT) | Total Amount in (BDT)
1 | Installation of Fire Alarm Cable | RM | 500 |  | 0
2 | Installation of PVC Pipe & Others Accessories | RM | 350 |  | 0
3 | Installation of Fire Alarm Control Panel | Lot | 1 |  | 0
4 | Installation of Battery for FACP | NOS |  |  | 0
5 | Installation of CO2 & ABC Types Extinguisher | NOS | 22 |  | 0
6 | Installation of Power Supply Unit | NOS | 1 |  | 0
7 | Installation of Additional Backbox for Detector, Module, Sounder & MCP. | NOS | 46 |  | 0
8 | Installation of Detectors, Modules, Sounder & Devices. | Nos. | 45 |  | 0
9 | As-Built Drawing & Documentation of Fire Detection & Alarm System | Job | 1 |  | 0
10 | Testing & Commissioning of Fire Detection & Alarm System including owner's representative training at site. | Job | 1 |  | 0
11 | Training | Job | 1 |  | 0
Sub-Total Amount BDT = |  |  |  |  | 0
Grand Total Amount BDT = |  |  |  |  | 0

## Summary
| Summary of | Value
1 | Electrical supply & Installation | 0
2 | FDS Main Items | 0
3 | FDS Local | 0
| Total | 0