ANNEX D

BGD-UNHCR RFP 3830

TECHNICAL SPECIFICATION FORMAT

FOR THE DESIGN, BoQ, SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF SOLAR PV HYBRID POWER SYSTEMS FOR TWO REFUGEE HIGHER EDUCATION CENTRES (RHECs), COX’S BAZAR – LOT 1: CAMP 4; LOT 2: CAMP 13

Lot: ☐ Lot 1 – RHEC Camp 4     ☐ Lot 2 – RHEC Camp 13

(submit one form per lot; if the offer is identical for both lots, tick both)

Instructions: complete the column “Bidder’s offer” for every line with the exact make, model and value offered, and indicate compliance (Y/N). Values must match the Technical BoQ (Annex B), the single line diagram and the datasheets. State the reference page in your technical offer where the evidence (datasheet, certificate, test report) can be found. Requirements marked “minimum” are mandatory; others are indicative and may be improved. No prices shall be included in this form.

1.	Solar PV modules

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer / country of origin / model | State; BloombergNEF Tier-1 (latest quarter) – attach evidence |  |  |  |
| 2 | Technology | Monocrystalline N-type (TOPCon or equivalent/higher) – minimum |  |  |  |
| 3 | Rated power per module / quantity / total kWp | ≥ 550 Wp per module; total ≥ 25 kWp – minimum |  |  |  |
| 4 | Module efficiency | ≥ 22% – minimum |  |  |  |
| 5 | Degradation | ≤ 1% year 1; ≤ 0.4% per year thereafter |  |  |  |
| 6 | Temperature coefficient (Pmax) | ≤ -0.35%/°C |  |  |  |
| 7 | Electrical data (Voc, Isc, Vmp, Imp) | State from datasheet |  |  |  |
| 8 | Junction box / connector | IP68 with bypass diodes / MC4-compatible |  |  |  |
| 9 | Frame / glass / dimensions / weight | Anodised aluminium; tempered AR glass; PID-resistant (IEC 62804); state mm and kg |  |  |  |
| 10 | Certification | IEC 61215, IEC 61730-1/-2, IEC 61701 (salt mist), IEC 62716; ISO 9001/14001/45001 manufacturer |  |  |  |
| 11 | Factory tests | Flash test and EL images for supplied batch (on delivery) |  |  |  |
| 12 | Labelling / traceability | Permanent label with serial number and QR/barcode |  |  |  |
| 13 | Warranty | Product ≥ 12 years; performance ≥ 25 years (state % at year 25) |  |  |  |

2.	Hybrid inverter(s)

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer / country / model / quantity | State |  |  |  |
| 2 | Type and rated AC output | Three-phase hybrid; total ≥ 20 kW – minimum |  |  |  |
| 3 | PV input: max DC voltage / MPPT range / number of MPPTs | State; ≥ 2 independent MPPTs |  |  |  |
| 4 | Battery interface: voltage range / max charge-discharge current | Compatible with offered LiFePO₄ BESS; state |  |  |  |
| 5 | Grid/generator input and transfer time | State; automatic changeover |  |  |  |
| 6 | Maximum / European efficiency | ≥ 98% / ≥ 96% |  |  |  |
| 7 | THD / power factor | < 3% / adjustable |  |  |  |
| 8 | Protections | Over/under voltage, overcurrent, short circuit, ground fault, anti-islanding, surge |  |  |  |
| 9 | IP rating / operating temperature | IP65 (or IP65 enclosure) / up to +50 °C without derating – state |  |  |  |
| 10 | Communication and monitoring | RS485/CAN/Ethernet/Wi-Fi; web portal and app |  |  |  |
| 11 | Certification | IEC 62109-1/-2, IEC 61000; IEC 61727 & IEC 62116 if grid-connected; CE or equivalent; BSTI-compliant import |  |  |  |
| 12 | Warranty / local service partner | ≥ 5 years / name and address of service centre in Bangladesh |  |  |  |

3.	Battery Energy Storage System (BESS)

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer / country / model / number of modules | State |  |  |  |
| 2 | Chemistry | LiFePO₄ – minimum |  |  |  |
| 3 | Gross / usable capacity | ≥ 150 kWh / ≥ 105 kWh – minimum |  |  |  |
| 4 | Nominal voltage and range | State |  |  |  |
| 5 | Usable depth of discharge used in design | ≥ 70% |  |  |  |
| 6 | Cycle life (state test conditions) | ≥ 6,000 cycles |  |  |  |
| 7 | Round-trip efficiency | ≥ 90% |  |  |  |
| 8 | Max continuous charge / discharge current (C-rate) | State |  |  |  |
| 9 | BMS functions and communication | Integrated smart BMS; CAN/RS485 to inverter |  |  |  |
| 10 | Enclosure / IP rating / cooling | Rack or cabinet; ≥ IP54; state |  |  |  |
| 11 | Fire safety | Fire-retardant enclosure; UL 9540A thermal-runaway test report (or equivalent) – attach |  |  |  |
| 12 | Certification | IEC 62619, UN 38.3, IEC 61000, UL 1973 or equivalent; BSTI-compliant import |  |  |  |
| 13 | Warranty | ≥ 10 years or equivalent throughput warranty (state MWh) |  |  |  |

4.	Mounting structure

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | Type (roof / ground) and material | HDG steel (zinc ≥ 80 µm, ISO 1461) or anodised aluminium |  |  |  |
| 2 | Fasteners | SS304, anti-theft |  |  |  |
| 3 | Design wind speed | Per latest edition of BNBC – BNBC-designated wind speed for the project location; state value used |  |  |  |
| 4 | Tilt / orientation | State |  |  |  |
| 5 | Structural calculation and drawings | To be submitted at design stage, signed by a structural engineer |  |  |  |
| 6 | Warranty / design life | ≥ 10 years / ≥ 25 years |  |  |  |

5.	Cables, distribution and protection

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | PV (DC) cables | IEC 62930 / EN 50618; tinned copper; UV and salt-mist resistant; state sizes |  |  |  |
| 2 | AC cables | IEC 60502; copper; state sizes; underground/conduit routing |  |  |  |
| 3 | Voltage drop (DC / AC) | ≤ 3% / ≤ 3% at design current – state calculated value |  |  |  |
| 4 | DC combiner / isolators / fuses | IP65; IEC 60947-3; gPV fuses IEC 60269-6 |  |  |  |
| 5 | AC distribution board / breakers / changeover | IP65 where outdoor; IEC 60947-2; automatic changeover/ATS |  |  |  |
| 6 | Surge protection (DC/AC) | Type II (Type I+II at main board if LPS installed) |  |  |  |
| 7 | Earthing | Copper-bonded; ≤ 5 Ω (max 10 Ω dry season) |  |  |  |
| 8 | Lightning protection | IEC 62305 risk assessment and system |  |  |  |

6.	Monitoring, fire safety and other components

| No. | Parameter | Minimum / indicative requirement | Bidder’s offer (make, model, value) | Y/N | Bid page ref. |
| --- | --- | --- | --- | --- | --- |
| 1 | Monitoring system / data logger | Web + app; PV, load, BESS SoC, grid/generator; alarms; UNHCR access |  |  |  |
| 2 | Fire detection and alarm (battery area) | Smoke and heat detectors, audible/visual alarm |  |  |  |
| 3 | Fire extinguishers | Class C (CO₂ / clean agent), quantity and location |  |  |  |
| 4 | Energy meter(s) | State |  |  |  |
| 5 | Other components (state each) | Datasheet, certification, warranty, manufacturer authorisation |  |  |  |

7.	Critical spare parts held in Bangladesh during the DLP

| No. | Item | Quantity | Storage location | Lead time if not in stock |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

COMPANY CONFIRMATION

We confirm that the equipment offered complies with all minimum requirements of the ToR (Annex A) except for any deviations listed below, that the values stated match our Technical BoQ, single line diagram and datasheets, and that no pricing information is included in this form.

Deviations (if none, state “None”): ____________________________________________

| Company name |  |
| --- | --- |
| Name of company representative |  |
| In the capacity of |  |
| Duly authorized to sign the bid for and on behalf of |  |
| Date |  |
| Signature and official stamp |  |