## Summary
BGD-UNHCR RFP 3830 – Annex E – Financial Offer Summary
Lot | Total excl. VAT (BDT) | VAT (BDT) | Total incl. VAT (BDT) | Bid submitted (Yes/No)
Lot 1 – RHEC Camp 4 | 0 | 0 | 0
Lot 2 – RHEC Camp 13 | 0 | 0 | 0
Each lot is evaluated and awarded separately; conditional discounts across lots will not be considered.

## E1 Lot 1 - Camp 4
BGD-UNHCR RFP 3830 Financial Offer Form / Priced BoQ – Lot 1 – RHEC Camp 4 Design, BoQ, Supply, Installation, Testing and Commissioning of Solar PV Hybrid Power Systems – Two RHECs, Cox’s Bazar
Annex E1 – Financial Offer Form | [7 empty] | Annex E (to be submitted separately)
SL | Item | Specification (as in Annex B) | Unit | Qty | Unit Price in BDT (excluding VAT) | Total Price in BDT (excluding VAT) | VAT Amount in BDT | Total Amount in BDT (including VAT)
1 | Solar PV modules – Monocrystalline N-Type or better/advanced technology, minimum 550 Wp per module, with total installed capacity meeting the design requirements (minimum 25 kWp). The stated specification shall be considered the minimum acceptable standard. |  | Pcs |  |  | 0 |  | 0
2 | Mounting structure incl. roof fixing and any structural strengthening |  | Lot |  |  | 0 |  | 0
3 | DC combiner / PV junction boxes with isolators, gPV fuses and SPDs |  | Set |  |  | 0 |  | 0
4 | PV (DC) cables and MC4 connectors |  | Meter |  |  | 0 |  | 0
5 | Three-phase hybrid inverter configuration with minimum combined inverter capacity of 20 kW. Bidders may propose one or multiple inverter units to achieve the required capacity and redundancy requirements. |  | Set |  |  | 0 |  | 0
6 | LiFePO₄ battery energy storage system incl. BMS, racks/cabinet (≥ 150 kWh gross / ≥ 105 kWh usable) |  | Set |  |  | 0 |  | 0
7 | Battery area works: enclosure/ventilation, smoke & heat detection with alarm |  | Lot |  |  | 0 |  | 0
8 | Fire extinguishers, Class C (CO₂ / clean agent) |  | Pcs |  |  | 0 |  | 0
9 | AC distribution board, automatic changeover/ATS, breakers and integration with existing MDB |  | Set |  |  | 0 |  | 0
10 | AC cables incl. trenching / conduit |  | Meter |  |  | 0 |  | 0
11 | Earthing system (array, inverter, BESS, boards) - Complete earthing system for solar array, inverter, battery energy storage system (BESS), distribution boards and all associated metallic structures. Design, installation and testing shall comply with the latest edition of BNBC and applicable IEC standards. Earthing bore depth shall be not less than 40 ft (12 m), subject to achieving the required earth resistance value. |  | Lot |  |  | 0 |  | 0
12 | Lightning protection system - Complete lightning protection system designed and installed in accordance with BNBC and IEC 62305, including air terminals, down conductors, bonding, surge protection devices (SPDs), dedicated earthing network, and testing. The design shall be supported by calculations and drawings submitted during the detailed design stage. |  | Lot |  |  | 0 |  | 0
13 | Monitoring system (data logger, communication, web portal and app) |  | Lot |  |  | 0 |  | 0
14 | Energy meter(s) |  | Pcs |  |  | 0 |  | 0
15 | Installation works, civil/structural works, labelling and signage |  | Lot |  |  | 0 |  | 0
16 | Testing, commissioning and Final Acceptance Test (IEC 62446-1) |  | Job |  |  | 0 |  | 0
17 | Training, O&M manual, SoP, as-built drawings and handover documents |  | Job |  |  | 0 |  | 0
18 | Critical spare parts held in Bangladesh for the DLP (Annex D, Section 7) |  | Lot |  |  | 0 |  | 0
19 | Defect Liability Period services – 12 months incl. quarterly preventive maintenance |  | Lot |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
| Total – Lot 1 – RHEC Camp 4 (BDT) |  |  |  |  | 0 | 0 | 0
Enter a price for every item of your Technical BoQ (Annex B), including any additional items. The total is a lump sum for the complete, fully functional system; all equipment, labour, transport, installation, testing, training, documentation, warranty and DLP obligations are deemed included.
Offer validity: 120 days from the submission deadline. Payment: per RFP Section 2.4.2 and ToR Section 14 (no advance payment).
NOTE: DO NOT SUBMIT THIS FORM WITH YOUR TECHNICAL OFFER. SUBMIT IT ONLY IN THE FINANCIAL SECTION OF THE CLOUD ERP NEGOTIATION.
DATE: ______________________________
NAME OF AUTHORISED COMPANY REPRESENTATIVE: ______________________________
SIGNATURE / STAMP OF THE COMPANY: ______________________________

## E2 Lot 2 - Camp 13
BGD-UNHCR RFP 3830 Financial Offer Form / Priced BoQ – Lot 2 – RHEC Camp 13 Design, BoQ, Supply, Installation, Testing and Commissioning of Solar PV Hybrid Power Systems – Two RHECs, Cox’s Bazar
Annex E2 – Financial Offer Form | [7 empty] | Annex E (to be submitted separately)
SL | Item | Specification (as in Annex B) | Unit | Qty | Unit Price in BDT (excluding VAT) | Total Price in BDT (excluding VAT) | VAT Amount in BDT | Total Amount in BDT (including VAT)
1 | Solar PV modules – Monocrystalline N-Type or better/advanced technology, minimum 550 Wp per module, with total installed capacity meeting the design requirements (minimum 25 kWp). The stated specification shall be considered the minimum acceptable standard. |  | Pcs |  |  | 0 |  | 0
2 | Mounting structure incl. roof fixing and any structural strengthening |  | Lot |  |  | 0 |  | 0
3 | DC combiner / PV junction boxes with isolators, gPV fuses and SPDs |  | Set |  |  | 0 |  | 0
4 | PV (DC) cables and MC4 connectors |  | Meter |  |  | 0 |  | 0
5 | Three-phase hybrid inverter configuration with minimum combined inverter capacity of 20 kW. Bidders may propose one or multiple inverter units to achieve the required capacity and redundancy requirements. |  | Set |  |  | 0 |  | 0
6 | LiFePO₄ battery energy storage system incl. BMS, racks/cabinet (≥ 150 kWh gross / ≥ 105 kWh usable) |  | Set |  |  | 0 |  | 0
7 | Battery area works: enclosure/ventilation, smoke & heat detection with alarm |  | Lot |  |  | 0 |  | 0
8 | Fire extinguishers, Class C (CO₂ / clean agent) |  | Pcs |  |  | 0 |  | 0
9 | AC distribution board, automatic changeover/ATS, breakers and integration with existing MDB |  | Set |  |  | 0 |  | 0
10 | AC cables incl. trenching / conduit |  | Meter |  |  | 0 |  | 0
11 | Earthing system (array, inverter, BESS, boards) - Complete earthing system for solar array, inverter, battery energy storage system (BESS), distribution boards and all associated metallic structures. Design, installation and testing shall comply with the latest edition of BNBC and applicable IEC standards. Earthing bore depth shall be not less than 40 ft (12 m), subject to achieving the required earth resistance value. |  | Lot |  |  | 0 |  | 0
12 | Lightning protection system - Complete lightning protection system designed and installed in accordance with BNBC and IEC 62305, including air terminals, down conductors, bonding, surge protection devices (SPDs), dedicated earthing network, and testing. The design shall be supported by calculations and drawings submitted during the detailed design stage. |  | Lot |  |  | 0 |  | 0
13 | Monitoring system (data logger, communication, web portal and app) |  | Lot |  |  | 0 |  | 0
14 | Energy meter(s) |  | Pcs |  |  | 0 |  | 0
15 | Installation works, civil/structural works, labelling and signage |  | Lot |  |  | 0 |  | 0
16 | Testing, commissioning and Final Acceptance Test (IEC 62446-1) |  | Job |  |  | 0 |  | 0
17 | Training, O&M manual, SoP, as-built drawings and handover documents |  | Job |  |  | 0 |  | 0
18 | Critical spare parts held in Bangladesh for the DLP (Annex D, Section 7) |  | Lot |  |  | 0 |  | 0
19 | Defect Liability Period services – 12 months incl. quarterly preventive maintenance |  | Lot |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
# | [[[[Add additional Items if required]]]] |  |  |  |  | 0 |  | 0
| Total – Lot 2 – RHEC Camp 13 (BDT) |  |  |  |  | 0 | 0 | 0
Enter a price for every item of your Technical BoQ (Annex B), including any additional items. The total is a lump sum for the complete, fully functional system; all equipment, labour, transport, installation, testing, training, documentation, warranty and DLP obligations are deemed included.
Offer validity: 120 days from the submission deadline. Payment: per RFP Section 2.4.2 and ToR Section 14 (no advance payment).
NOTE: DO NOT SUBMIT THIS FORM WITH YOUR TECHNICAL OFFER. SUBMIT IT ONLY IN THE FINANCIAL SECTION OF THE CLOUD ERP NEGOTIATION.
DATE: ______________________________
NAME OF AUTHORISED COMPANY REPRESENTATIVE: ______________________________
SIGNATURE / STAMP OF THE COMPANY: ______________________________